## Version Control
Version Control
| Version | Description | Date
| V1 | Initial publication at ITT launch | 16 July 2025
| V2 | Updated version during the ITT Stage. Additional questions have been added to both the "A.Solution Outline" tab and "B.Feasibility Simulation" tab. These are marked with a V2 indicator. | 22 August 2025
| V3 | Updated version during the ITT Stage. Clarification for solutions part of a larger installation. Updates are marked with a 'V3' indicator. | 12 September 2025
| V4 | Updated version during the ITT Stage to provide clarity on the stability feasibility simulation requirements for 0MW solutions. | 18 November 2025

## Introduction
Long-term 2029 Tender
Stability Service Technical Submission
Introduction
This document should be used to respond to the stability service technical questions where a bidder is bidding in for the Stabiltiy Service as part of the Long-term 2029 tender. This document should be read in conjunction with the relevant sections of the other ITT documents. This document should be completed in full. Failure to complete this document in full may result in your submission being rejected. Tenderers must not amend this document in anyway. Should tenderers amend this document NESO reserve the right the reject your tender submission.
Please refer to the Instructions to Tenderers for the ITT submission deadline. Tenderers should submit their response using the Ariba platform.
Instructions
Section A: Solution Outline must be completed, responding to each question for each Solution being proposed.
Section B: Feasibility Simulation must be completed, responding to each question for each Solution being proposed.
Section C: DRC Data should be provided based on the details of this tab.
The cap on solutions must not be exceeded.
Tenderers should only fill in the cells highlighted in light blue.
Please confirm using the drop box below that you understand and agree with the following conditions
I have completed the Stability Technical Submission document fully and accurately to the best of my knowledge.
I understand that to be considered for provision of the stability service under the long-term 2029 contract I must pass all pass/fail requirements.
I understand and agree that NESO reserve the right (but not the obligation) to publish key parameters of this bid when publishing the tender results

## A Solution Outline
Section A: Stability Service Technical Compliance Assessment - Solution Outline
Please provide us information on the technological solution you intend to offer for the stability service. Tenderers are able to submit a number of solutions in line with the cap. Please use a separate column to respond for each solution. The number of solutions should not exceed the solution cap.
| No. | Question/Information Required | Scoring Methodology | Scoring Criteria | Response format | Solution 1 | Solution 2 | Solution 3 | Solution 4 | Solution 5 | Solution 6 - Please add additional columns for additional solutions as required
| Please enter a solution reference number for each proposed solution using the reference convention provided. This will be the solution identifier throughout the tender assessment process. |  |  |  |  | [Company Name]-Bid1 | [Company Name]-Bid2 | [Company Name]-Bid3 | [Company Name]-Bid4 | [Company Name]-Bid5 | [Company Name]-Bid6
| For each solution please confirm the company name that would enter the contract for this solution (this should match what is provided in the pricing submission proforma) |  |  |  |  | [Contracting Entity] | [Contracting Entity] | [Contracting Entity] | [Contracting Entity] | [Contracting Entity] | [Contracting Entity]
Eligibility Criteria Questions
| 1 | Please confirm that the solution is within a region of need. | Pass/Fail | Pass = the solution is within one of the defined regions of need Fail = the solution is not within one of the defined regions of need, or there is insufficient explanation about which substation the solution will connect to, leaving NESO with uncertainty Responses to Q2 will be taken into account when scoring this question. | State yes or no and explain which substation, or which point on the transmission system, that the solution is connected to/ intends to directly or radially connect to. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 2 | Please state which region (s) of need this solution falls into | For information. Response will be used to inform the scoring of Q1 above | For information. Response will be used to inform the scoring of Q1 above | Please also state which region (s) of need it falls into, based on the stability technical specification and effectiveness documents | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 3 | How do you expect to meet 90% availability for the declared stability capability (both SCL and inertia)? | For Information. The response will be used to inform the scoring of Q4 | For Information. The response will be used to inform the scoring of Q4 | Provide justification/rationale based on the following: technology/connection details/expectations/limitations. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 4 | Can the solution meet the 90% minimum availability criteria for the declared stability capability (both SCL and inertia)? | Pass/Fail | Pass = The bidder has stated yes and provided sufficient explanation and evidence to demonstrate that the 90% availability requirement can be met Fail = The bidder has stated no, the solution cannot meet the 90% availability criteria, or the bidder has stated yes but does not provide sufficient explanation and evidence that the 90% availability requirement can be met Responses to Q3 will be taken into account when scoring this question. | State yes/no. If stating no, provide additional information on why you can not meet this criteria. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 5 | Does the solution have any agreements which include an intertripping scheme, including but not limited to a System to Generator Operational Intertripping Scheme Category 1 or Category 3 ? For the purpose of this question, protection and control (P&C) is not included. | For Information. The response will be used to inform the scoring of Q6 | For Information. The response will be used to inform the scoring of Q6 | Please state and detail any interipping scheme. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 6 | Please confirm that the connection design of the solution will not impede its ability to maintain 90% availability? | Pass/fail | Pass = The bidder has stated yes and provided sufficient explanation/evidence to demonstrate that the connection design will not affect the availability of the solution and ability to meet the 90% availability requirement Fail = The bidder has stated no, or the bidder has stated yes but there is insufficient explanation/evidence provided to demonstrate that the connection design will not affect the availability of the solution and ability to meet the 90% availability requirement Responses to Q5 will be taken into account when scoring this question. | Yes/No with an explanation of your connection design and how it enables your availability | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 7 | Please confirm whether your solution is 1) new, 2) providing additional capability through incremental investment or 3) an existing asset that can operate at 0MW or independently of MW Note: the definitions for each of these terms are as per the Stability Techncial Specification | Pass/fail | Pass = Solution is either new, providing additional capability through incremental investment or an existing asset, and in any case the bidder has provided sufficient explanation/evidence to demonstrate it meets the definitions as per the Stability Techncial Specification Fail = Solution is not new, providing additional capability through incremental investment or an existing asset that can operate at 0MW or independently of MW; or the bidder has not provided sufficient explanation/evidence to demonstrate this based on the definitions as per the Stability Techncial Specification Response to Q8 will be taken into account when scoring this question. | Please state whether your solution is "new", "providing additional capability thorugh incremental investment" or "an existing asset" | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 8 | Further to Q7, please explain how your solution is either 1) new, 2) providing additional capability through incremental investment or 3) an existing asset based on the definitions in the Stability Technical Specification | For Information. The response will be used to inform the scoring of Q7 | For Information. The response will be used to inform the scoring of Q7 | Free text explanation | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 9 | Please confirm that your solution is not fitted with RoCoF protection relays or any other equipment that may impede your solutions ability to supply Active RoCoF Response Power | Pass/Fail | Pass = Sufficient explanation or evidence provided that there are no or there will be no RoCoF protection relays or other equipment that may impede the Active RoCoF Response Power Fail = Insufficient evidence or explanation that there are no or there will be no RoCoF protection relays or other equipment that may impede the Active RoCoF Response Power; or it is confirmed there is going to be RoCoF protection relays/equipment that may impede the Active RoCoF Response Power. | Free text explanation | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 10 | If the solution is GBGF-S can the inertia service be provided at 0MW export? | Pass/Fail/Not Applicable | Pass = The inertia service can provided at 0MW export Fail = The inertia service cannot be provided at 0MW export Not Applicable = the solution is not GBGF-S | Yes/No/Not Applicable | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
Technology Questions
| 11 | What is the technology type of your proposed solution? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | e.g. synchronous/ grid forming converter/ other (if other please describe) | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 12 | Who is the Original Equipment Manufacturer (OEM) of your proposed solution? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Please state your OEM and provide any supporting OEM documents about your solution | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 13 | Is there anything else you would like to tell us about this technology? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Free text | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 14 | Please confirm that you have provided a single line diagram as an attachment to this Technical submission document V3 This must cover the whole installation where applicable. | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | State yes/no. If yes, please state the document reference of the provided single line diagram. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 15 | What is the MVA rating of the proposed solution? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Please state the rating in MVA. If the solution comprises of multiple units, please state the rating of each unit. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 16 | What is your expected active power export during normal operation (MW)? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | State in MW. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 17 | What is your expected power consumption during normal operation (MW)? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | State in MW. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 18 | Can the proposed solution provide the Short Circuit Level response as defined in the Technical Specification? | Pass/Fail | Pass = Yes with sufficient explanation provided to demonstrate capability Fail = No, or Yes with insufficient explanation of capability | State yes/no and provide justification for your response. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 19 | Are there any limitations on your solution's repeated ability to provide Fast Fault Current Injection? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Free text | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 20 | What is the peak current rating of the proposed solution as defined in the technical specification? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Free text | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 21 | How does your SCL availability relate to your steady state active power and/or reactive power output? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Describe any dependencies | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 22 | Can the proposed solution provide an inertia response as defined in the technical specification? This includes being able to deliver the inertia response for as long as the service is instructed. | Pass/Fail | Pass = Yes with sufficient explanation provided to demonstrate capability Fail = No, or Yes with insufficient explanation of capability | State yes/no and provide justification for your response. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 23 | Is the inertia provided by the solution greater than 100 MVA.s but less than 5 GVA.s? | Pass/Fail | Pass = solution is within the size limits for inertia Fail = solution is not within the size limits set for inertia | V2 State yes/no and provide the size of the solution. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 24 | If the solution is GBGF-I, is the H-constant value below or equal to 25? | Pass/fail | Pass = Yes with sufficient explanation provided to demonstrate capability Fail = No, or Yes with insufficient explanation of capability | V2 State yes/no and provide the H-Constant of the solution. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 25 | How does your inertia availability relate to your steady state active power and/or reactive power output? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information We reserve the right to use the response to this question to inform scoring of other questions | Describe any dependencies | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 26 | Does the provision of the inertia and SCL exceed the peak current rating of your solution? | Pass/fail | Pass = Yes with sufficient explanation provided to demonstrate capability Fail = No, or Yes with insufficient explanation of capability | State yes/no and provide justification for your response. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 27 | Can the solution provide an osccilation damping capability as stated in the technical specification? | Pass/Fail | Pass = Yes with sufficient explanation of capability will be achieved Fail = No, or Yes with insufficient expalantion of capability | State yes/no and provide justification for your response. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 28 | Please explain how your solution meets the relevant Grid Forming requirements in ECC.6.3.19 | Pass/Fail | Pass = Yes with sufficient explanation or evidence of how the solution meets the relevant requirements in ECC.6.3.19 Fail = No, solution does not meet ECC.6.3.19; or Yes but there is insufficient explanation or evidence provided to demonstrate that the relevant requirements of ECC.6.3.19 are met | V2 State yes/no and provide an explanation for your response, including an explanation for any limitations your solution might have. This answer should take the format of a full written answer, where any external documents that are referred to should be referenced clearly and concisely, with any relevant page numbers and sections clearly referenced. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 29 | For GBGF-I solutions does your solution have any Grid Following components? If so please explain the operation of these elements within your solution. | Pass/Fail | Pass = Yes with sufficient explanation provided to demonstrate capability Fail = No, or Yes with insufficient explanation of capability | V2 State yes/no and provide an explanation for your response, including an explanation for any limitations your solution might have. This answer should take the format of a full written answer, where any external documents that are referred to should be referenced clearly and concisely, with any relevant page numbers and sections clearly referenced. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 30 | Is your solution able to operate at Zero Short Circuit Level (ECC.6.3.19.4 (ii)) | Pass/Fail | Pass = Yes with sufficient explanation provided to demonstrate capability Fail = No, or Yes with insufficient explanation of capability | V2 Free text, please provide a justifcation to your response. Where any external documents that are referred to should be referenced clearly and concisely, with any relevant page numbers and sections clearly referenced. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 31 | For GBGF-I solutions, please explain your inverter characteristics, i.e. does the solution need to reserve inverter headroom, or is the inverter capable of overloading? | For Information We reserve the right to use the response to this question to inform scoring of other questions | For Information. We reserve the right to use the response to this question to inform scoring of other questions | V2 Please describe any dependencies for reserving headroom on your inverter for the delivery of Inertia. Within your response please refer to your feasibility study and reference any relevant manufacturer data sheets. This answer should take the format of a full written answer, where any external documents that are referred to should be referenced clearly and concisely, with any relevant page numbers and sections clearly referenced. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 32 | For GBGF-I solutions please describe the following: - The operation of your technology - How your solution can be represented as a voltage source behind a real physical impedance (ECC.6.3.19.3 (ii)) -The delivery of active power from your solution with reference to the Internal Voltage Source | Pass/Fail/Not Applicable | Pass = Description meets ECC.6.3.19 Fail = Description does not meet ECC.6.3.19 Not Applicable = the solution is not GBGF-I | V2 Describe the operation of the solution and it's representation as a voltage source behind a real physical impedance (Please include a circuit diagram). Responses should explain how the solution delivers active power with reference to it's internal voltage source. Please refer to any relevant manufacturer data sheets that will support this answer. It is expected that a circuit diagram is included as part of your answer. This answer should take the format of a full written answer, where any external documents that are referred to should be referenced clearly and concisely, with any relevant page numbers and sections clearly referenced. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 33 | Does your solution have an AC connection to the main GB synchronous transmission system? | Pass/Fail | Pass = Yes Fail = No | Yes/No | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 34 | V2 Please confirm the type of connection design for your solution | V2 For Information We reserve the right to use the response to this question to inform scoring of other questions | V2 For Information We reserve the right to use the response to this question to inform scoring of other questions | V2 Please list the connection type: E.g Grid Park . Please also state if the connection is non-firm | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
` | 35 | Does the proposed solution meet the full technical specification? Are there any limitations with regards to meeting the technical requirements? | Pass/Fail | Pass = Yes with sufficient demonstration of capability that solution meets technical specification throughout technical submission Fail = No, the solution doesn't meet technical specification or there is insufficient demonstration that the solution meets the technical specification throughout the technical submission NESO reserve the right to consider responses to all of the stability criteria questions in this proforma when scoring this question. | State yes/no. Provide additional information of any limitations and mitigations. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
Reserved Bay Questions
| 36 | Is the MW of your solution within the capacity stated for the site? | Pass/Fail specific to solutions using reserved bays | Pass = Yes with explanation to demonstrate the solution size is within the capacity stated for the site Fail = The capacity is not within the capacity of the site, or there is insufficient explanation provided | Yes/no. Please state your MW capacity and the capacity of the site. Please provide additional information if necessary | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 37 | Is the MVAr of your solution within the capacity stated for the site? | Pass/Fail specific to solutions using reserved bays | Pass = Yes with explanation to demonstrate the solution size is within the capacity stated for the site Fail = The capacity is not within the capacity of the site, or there is insufficient explanation provided | Yes/no. Please state your Mvar capacity and the capacity of the site. Please provide additional information if necessary | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 38 | Are both the Sub-transient SCL (Sk") and the Transient SCL (Sk') of the solutions within the values we have assumed for the reserved bay(s)? | Pass/Fail specific to solutions using reserved bays | Pass = Yes* Fail = No | Yes / No * Further checks will need to be carried out where Sk" and Sk' are within the limits but the X"/R is exceeded. Depending on findings the solution may be failed. | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
Stacking due diligence
| 39 | If you intend to stack the Commercial Frequency Response service, please explain how your solution will be able to stack this service without impacting the solution's ability to also provide the stability service | Pass/Fail/Not Applicable | Pass = sufficient explanation provided that the Commercial Frequency Response service could be stacked without impacting the ability to also provide the stability service Fail = insufficient explanation provided to demonstrate that the Commercial Frequency Response service could be stacked without impacting the ability to also provide the stability service Not Applicable = bidder does not intend to stack the Commercial Frequency Response service | Free text response | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 40 | If you intend to stack the Reserve service, please explain how your solution will be able to stack this service without impacting the solution's ability to also provide the stability service | Pass/Fail/Not Applicable | Pass = sufficient explanation provided that the Reserve service could be stacked without impacting the ability to also provide the stability service Fail = insufficient explanation provided to demonstrate that the Reserve service could be stacked without impacting the ability to also provide the stability service Not Applicable = bidder does not intend to stack the Reserve service | Free text response | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 41 | If you intend to stack the Reactive Power Service, please explain how your solution will be able to stack this service without impacting the solution's ability to also provide the stability service | Pass/Fail/Not Applicable | Pass = sufficient explanation provided that the Reactive Power service could be stacked without impacting the ability to also provide the stability service Fail = insufficient explanation provided to demonstrate that the Reactive Power service could be stacked without impacting the ability to also provide the stability service Not Applicable = bidder does not intend to stack the Reactive Power service | Free text response | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 42 | If you intend to stack the CMIS service, please explain how your solution will be able to stack the CMIS service on the basis of quick de-load capability (or an alternative capability) to maintain the stability service in the event the CMIS service is armed | Pass/Fail/Not Applicable | Pass = sufficient explanation provided that the CMIS service could be stacked without impacting the ability to also provide the stability service Fail = insufficient explanation provided to demonstrate that the CMIS service could be stacked without impacting the ability to also provide the stability service Not Applicable = bidder does not intend to stack the CMIS service | Free text response | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here
| 43 | If you are an interconnector, have your underlying "Operational Procedures" been updated to allow provision of stability services in line with the stability technical specification? | Pass/Fail/Not Applicable | Pass = sufficient demonstration that the interconnector's underlying "Operational Procedures" have been updated and agreed to enable provision of the stability service Fail = insufficient evidence or demonstration that the interconnector's underlying "Operational Procedures" have been updated and agreed to enable the provision of the stability service Not applicable = the solution is not an interconnector | Free text response | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here | Enter response here

## B. Feasibility Simulation
Section B: Stability Service Compliance Assessment - Feasibility Simulation
Tenderers are required to complete feasibility studies in line with the Feasibility StudyRequirements document, and submit a copy of the feasibility study report as part of this tender. Please answer each question below in relation to the feasibility study report. Tenderers are requested to note the page number of the feasibility study report that corresponds to each question. Tenderers are able to submit a number of solutions in line with the cap. Please use a separate column to respond for each solution. The number of solutions should not exceed the solution cap. Pass/Fail decisions for these questions will be determined based on both the answers to the questions below and what is demonstrated in the feasibility study report that is submitted.
[5 empty] | Solution 1 |  | Solution 2 |  | Solution 3 |  | Solution 4 |  | Solution 5 |  | Solution 6 - please add additional columns for additional solutions as required
[5 empty] | [Company Name]-Bid1 |  | [Company Name]-Bid2 |  | [Company Name]-Bid3 |  | [Company Name]-Bid4 |  | [Company Name]-Bid5 |  | [Company Name]-Bid6
[5 empty] | [Contracting Entity |  | [Contracting Entity |  | [Contracting Entity |  | [Contracting Entity |  | [Contracting Entity |  | [Contracting Entity
No. | Category | Question/Information required | Scoring Methodology | Response format | Response | Page number | Response | Page number | Response | Page number | Response | Page number | Response | Page number | Response | Page number
44 | General | Are the technical study assumptions provided in the report? | Pass/Fail | Yes, No
45 | General | Are all the parameters of the network up to the Grid Entry Point provided? | Pass/Fail | Yes, No
46 | General | Is the equivalent system modelled as per the impedance and X/R values from the Stability Connection Data Sheet | Pass/Fail | Yes, No
47 | General | What is the time step adopted in the simulations? | Pass/Fail | Time step in milliseconds
48 | General | Are results recorded up to a period of reaching post fault steady state? | Pass/Fail | Yes, No
49 | General | Are voltage magnitude and angle at the Grid Entry Point recorded? | Pass/Fail | Yes, No
50 | General | Are total active current and reactive current from the solution at the Grid Entry Point recorded? | Pass/Fail | Yes, No
51 | General | Are active and reactive power from the solution at the Grid Entry Point recorded? | Pass/Fail | Yes, No
52 | General | Are solution terminal voltage angle and magnitude recorded? | Pass/Fail | Yes, No
53 | General | Are pre event conditions at the solution provided for all tests (voltage, total current, active current, reactive current, apparent power, active power and reactive power)? | Pass/Fail | Yes, No
54 | General | Are measurements dataset files regarding all results provided for all tests? | Pass/Fail | Yes, No
55 | General | Have model settings, transformer tap, and controller's parameters remained unchanged for all tests? If changes were made, has NESO agreed with these changes? | Pass/Fail | Yes, No
56 | General | Is the method to calculate RMS from EMT results clearly stated (Applicable for GBGF-I and Hybrid solutions only)? | Pass/Fail | Yes, No
57 | General | Has the MVAr range been provided in Table 2 of the feasibility study report template? Is this range compliant with the relevant section of ECC.6.3.2 and/or the technical specification. | Pass/Fail | Yes, No
58 | General | Have the tests been carried out using the correct operation points (Maximum active power import/export, Maximum reactive power import/export) | Pass/Fail | Yes, No
59 | General | Have LFSM and FSM been disabled during the tests? | Pass/Fail | Yes, No
60 | General | V3 If the solution is a part of a wider installation, has other plant that does not form part of the proposed solution been considered in the modelling correctly? | Pass/Fail/Not Applicable | Yes, No, Not Applicable
61 | General | V3 If the solution is a part of a wider installation, are the results presented such that the other plant's performance can be observed for all tests? | Pass/Fail/Not Applicable | Yes, No, Not Applicable
62 | General | V3 If the solution is a part of a wider installation, are the results presented such that the other plant's performance is subtracted from any provided quantities? | Pass/Fail/Not Applicable | Yes, No, Not Applicable
63 | Test 1 | Is Test 1 performed for all MW/MVAr combinations (Steps 1-7)? | Pass/Fail | Yes, No
64 | Test 1 | What Step from Steps 1-7 has resulted in the lowest short circuit reactive current injection at the Grid Entry Point (worst case)? | For information | State the step number corresponding to the lowest short circuit current contribution
65 | Test 1 | Do Steps 1-7 results show a response time equal or lower than 5 ms? | Pass/Fail | Yes, No
66 | Test 1 | For GBGF-I, do Steps 1-7 results show the peak current being provided no later than 30 ms after the fault occurence? | Pass/Fail | Yes, No
67 | Test 1 | Has the solution tripped for Test 1? | Pass/Fail | Yes, No
68 | Test 1 | From Steps 1-7, what is the minimum RMS positive sequence reactive short circuit contribution at 40ms? | For information This will be applied during the economic assessment and contract | State in kA
69 | Test 1 | Is the reactive/total fault current injected at the Grid Entry Point provided at Table 3 of the feasibility study report template? | Pass/Fail | Yes, No
70 | Test 1 | Is the fault current provided in Table 3 the positive sequence value at 40 ms after the fault? | Pass/Fail | Yes, No
71 | Test 1 | V2 Have steps 1-7 of Test 1 been completed correctly and are all required time-series plots included? | Pass/Fail | Yes,No
72 | Test 1 | Is Step 8a performed with the worst case condition from Steps 1-7? | For Information | Yes, No, Not Applicable
73 | Test 1 | Which reference node is considered for Step 8? | For Information | State which reference node is considered
74 | Test 1 | Do the step 8 results show a response time equal or lower than 5 ms? | Pass/Fail | Yes, No, Not Applicable
75 | Test 1 | Is the fault modelled in Step 8 as per the fault impedance provided by NESO? | Pass/Fail | Yes, No, Not Applicable
76 | Test 1 | Is the reactive/total fault current injected at the Grid Entry Point provided at Table 3 of the feasibility study report template? | Pass/Fail | Yes, No, Not Applicable
77 | Test 1 | Is the fault current provided in Table 3 the positive sequence value at 40 ms after the fault? | Pass/Fail | Yes, No, Not Applicable
78 | Test 1 | From Step 8a, what is the reactive RMS positive sequence fault current contribution at 40 ms for a remote fault at the reference locations? | For information This will be applied during the economic assessment and contract | State in kA
79 | Test 1 | Is Step 8a performed with the worst case condition from Steps1-7? | Pass/Fail | Yes, No, Not Applicable
80 | Test 1 | Which reference node is considered for Step 8a? | For Information | State which reference node is considered
81 | Test 1 | Do the step 8a results show a response time equal or lower than 5 ms? | Pass/Fail | Yes, No, Not Applicable
82 | Test 1 | Is the fault modelled in Step 8a as per the fault impedance provided by NESO? | Pass/Fail | Yes, No, Not Applicable
83 | Test 1 | Is the reactive/total fault current injected at the Grid Entry Point provided at Table 3 of the feasibility study report template? | Pass/Fail | Yes, No, Not Applicable
84 | Test 1 | Is the fault current provided in Table 3 the positive sequence value at 40 ms after the fault? | Pass/Fail | Yes, No, Not Applicable
85 | Test 1 | From Step 8b, what is the reactive RMS positive sequence fault current contribution at 40 ms for a remote fault at the reference locations? | For information This will be applied during the economic assessment and contract | State in kA
86 | Test 1 | Is Step 8b performed with the worst case condition from Steps1-7? | Pass/Fail | Yes, No, Not Applicable
87 | Test 1 | Which reference node is considered for Step 8b? | For Information | State which reference node is considered
88 | Test 1 | Do the step 8b results show a response time equal or lower than 5 ms? | Pass/Fail | Yes, No, Not Applicable
89 | Test 1 | Is the fault modelled in Step 8b as per the fault impedance provided by NESO? | Pass/Fail | Yes, No, Not Applicable
90 | Test 1 | Is the reactive/total fault current injected at the Grid Entry Point provided at Table 3 of the feasibility study report template? | Pass/Fail | Yes, No, Not Applicable
91 | Test 1 | Is the fault current provided in Table 3 the positive sequence value at 40 ms after the fault? | Pass/Fail | Yes, No, Not Applicable
92 | Test 1 | From Step 8c, what is the reactive RMS positive sequence fault current contribution at 40 ms for a remote fault at the reference locations? | For information This will be applied during the economic assessment and contract | State in kA
93 | Test 1 | Is Step 8c performed with the worst case condition from Steps1-7? | Pass/Fail | Yes, No, Not Applicable
94 | Test 1 | Which reference node is considered for Step 8c? | For Information | State which reference node is considered
95 | Test 1 | Do the step 8c results show a response time equal or lower than 5 ms? | Pass/Fail | Yes, No, Not Applicable
96 | Test 1 | Is the fault modelled in Step 8c as per the fault impedance provided by NESO? | Pass/Fail | Yes, No, Not Applicable
97 | Test 1 | Is the reactive/total fault current injected at the Grid Entry Point provided at Table 3 of the feasibility study report template? | Pass/Fail | Yes, No, Not Applicable
98 | Test 1 | Is the fault current provided in Table 3 the positive sequence value at 40 ms after the fault? | Pass/Fail | Yes, No, Not Applicable
99 | Test 1 | From Step 8d, what is the reactive RMS positive sequence fault current contribution at 40 ms for a remote fault at the reference locations? | For information This will be applied during the economic assessment and contract | State in kA
100 | Test 1 | Is Step 8d performed with the worst case condition from Steps1-7? | Pass/Fail | Yes, No, Not Applicable
101 | Test 1 | Which reference node is considered for Step 8d? | For Information | State which reference node is considered
102 | Test 1 | Do the step 8d results show a response time equal or lower than 5 ms? | Pass/Fail | Yes, No, Not Applicable
103 | Test 1 | Is the fault modelled in Step 8d as per the fault impedance provided by NESO? | Pass/Fail | Yes, No, Not Applicable
104 | Test 1 | Is the reactive/total fault current injected at the Grid Entry Point provided at Table 3 of the feasibility study report template? | Pass/Fail | Yes, No, Not Applicable
105 | Test 1 | Is the fault current provided in Table 3 the positive sequence value at 40 ms after the fault? | Pass/Fail | Yes, No, Not Applicable
106 | Test 1 | V2 Has Step 8 been completed correctly and are all required time-series plots included? | Pass/Fail | Yes, No, Not Applicable
107 | Test 1 | V2 Please provide an explanation of how the performance in Test 1 meets the requirements in the Technical Specification | Pass/Fail | Please provide an explanation of the performance
108 | Test 2 | Is Test 2 performed for all MW/MVAr combinations (1-8)? | Pass/Fail | Yes, No
109 | Test 2 | Is the inertia (MVA.s) value explained through calculations for Steps 1-8? | Pass/Fail | Yes, No
110 | Test 2 | Is the inertia (MVA.s) values computed for Steps 1-8 based on average power change during the event? | Pass/Fail | Yes, No
111 | Test 2 | Has the solution tripped or hit any limit for Steps 1-8? | Pass/Fail | Yes, No
112 | Test 2 | Is the reactive power range used for the simulation consistent with the data provided in Table 2. | Pass/Fail | Yes, No
113 | Test 2 | V2 Please explain the cause of any changes in the reactive power during the RoCoF events. Please comment on this performance with relation to part 4 of section 4.3 of the technical specification. | Pass/Fail | Please provide an explanation of the performance
114 | Test 2 | Does Step 1-9 results show a response time equal or lower than 5 ms? (Please provide a zoomed in graph of Step 9 showing this response time) | Pass/Fail | Yes, No
115 | Test 2 | Are inertia values computed for Steps 1-8 presented in Table 4 of the feasibility study report template? | Pass/Fail | Yes, No
116 | Test 2 | Is the minimum inertia value presented in Table 4 of the feasibility study report template? | Pass/Fail | Yes, No
117 | Test 2 | For GBGF-S, is the inertia value provided by the manufacturer presented? | Pass/Fail | Yes, No
118 | Test 2 | From Steps 1-8, what is the minimum inertia (MWs) value? | For information This will be applied during the economic assessment and contract | State in MWs Please provide evidence of the minimum inertia through the feasibility simulation (Test 2)
119 | Test 2 | What Step from Steps 1-8 has resulted in the lowest inertia at the Grid Entry Point or User System Entry Point? | For information | State the step number corresponding to the lowest inertia value (S# or I#)
120 | Test 2 | Is a Time Series plot of Test 10 Included? | Pass/Fail | Yes,No
121 | Test 2 | Is a Time Series plot of Test 11 Included? | Pass/Fail | Yes,No
122 | Test 2 | V2 Is a Time Series plot of Test 12 Included? | Pass/Fail | Yes,No
123 | Test 2 | V2 Is a Time Series plot of Test 13 Included? V4 Not Applicable for 0MW Solutions | Pass/Fail | V4 Yes,No,Not Applicable
124 | Test 2 | V2 Is a Time Series plot of Test 14 Included? | Pass/Fail | Yes,No
125 | Test 2 | V2 Is a Time Series plot of Test 15 Included? V4 Not Applicable for 0MW Solutions | Pass/Fail | V4 Yes,No,Not Applicable
126 | Test 2 | V4 Have all the required Steps of Test 2 been completed correctly and are all required time-series plots included? | Pass/Fail | Yes,No
127 | Test 2 | V2 Please provide an explanation of how the performance in Test 2 meets the requirements in the Technical Specification | Pass/Fail | Please provide an explanation of the performance
128 | Test 2 | Is the maximum number of repeated inertial responses that can be provided for successive frequency events of either +1Hz/s or -1Hz/s lasting for 1 second each without having to charge/discharge equal to 5 or more? | For information, we reserve the right to use this in the scoring of other questions. | Yes, No If No, state the number of successive events
129 | Test 2 | Is the response of the plant compliant with the requirements of ECC.6.3.19? | Pass/Fail | State Yes,No and provide an explanation for the response.
130 | Test 3 | Is the reactive power range used for the simulation consistent with the data provided in Table 2. | Pass/Fail | Yes, No
131 | Test 3 | Has the solution tripped or blocked for steps 1-4? | Pass/Fail | Yes, No
132 | Test 3 | Has the solution tripped or blocked for steps 5-6? | Pass/Fail | Yes, No
133 | Test 3 | V2 Has the solution tripped or blocked for steps 7-10? | Pass/Fail | Yes, No
134 | Test 3 | V2 Has the solution tripped or blocked for steps 11-12? | Pass/Fail | Yes, No
135 | Test 3 | V2 Has the solution tripped or blocked for steps 13-16? | Pass/Fail | Yes, No
136 | Test 3 | V2 Has the solution tripped or blocked for steps 17-18? | Pass/Fail | Yes, No
137 | Test 3 | V2 Has the solution tripped or blocked for steps 19-22? | Pass/Fail | Yes, No
138 | Test 3 | V2 Has the solution tripped or blocked for steps 23-24? | Pass/Fail | Yes, No
139 | Test 3 | V2 Have Steps 1-24 of Test 3 been completed correctly and are all required time-series plots included? | Pass/Fail | Yes, No
140 | Test 3 | V2 Is an explanation of the performance of the plant provided? Noting this must include an explanation of how any limiters are implemented. | Pass/Fail | Yes, No
141 | Test 3 | V2 Please provide an explanation of how the performance in Test 3 meets the requirements in the Technical Specification | Pass/Fail | Please provide an explanation of the performance
142 | Test 3 | Is the test summary provided in Table 5 of the feasibility study report template? | Pass/Fail | Yes, No
143 | Test 3 | Is the response of the plant compliant with the requirements of ECC.6.3.19? | Pass/Fail | State Yes,No and provide an explanation for the response.
144 | Test 3 | Is the response of the plant inherent, providing a response within 5ms? | Pass/Fail | State Yes,No and provide an explanation for the response.

## C. DRC Data
DRC Data required for Long-Term 2029
The data is required for each solution that has been proposed in the tender even if it has an existing connection.
The data needs to be provided in excel format. Use the link below for a previous DRC tool that bidders can use to enable submission of DRC Data:
Download DRC Tool
Unless any data entry states "No" in the field titled 'Essential at the application stage' , the data within the DRC form is required.
The data must be provided based on technology type e.g. synchronous machine data needs to filled for synchronous compensators.
Note: NESO are in the process of upgrading how DRC data should be provided as part of the connections process (see here https://www.neso.energy/industry-information/connections/drc-generator-portal#Introduction-to-DRC ) for the purpose of this tender however, please return DRC in an excel spreadsheet based on the above tool.
Submission format
This is to be provided as part of the technical submission. NESO recommend submitting a master DRC zip folder, including a DRC datasheet document for each proposed solution
Please name each DRC data file in accordance with the solution references used through this document e.g. [Company Name]-Bid1
Useful links to fill DRC data:
https://www.neso.energy/document/34021/download
This data will not be scored or assessed directly but may be used to inform NESO's understanding of solution capability and scoring of other tender criteria.