Stability Service Technical Feasibility Study Report Template.

Long Term 2029 Stability Service.

Information that is supplied to Tenderers as part of this ITT is supplied in good faith. The information contained in the ITT Tender Pack and in any related written or oral communication is believed to be correct at the time of issue but NESO will not accept any liability for its accuracy, adequacy or completeness and no warranty is given as such. Any reliance by a Tenderer or any third party on the information provided by NESO as part of this ITT is at the Tenderer’s and/or third party’s risk.

Version Control

| Version Number | Date | Notes |
| --- | --- | --- |
| V1 | 16 July 2025 | Initial version published at ITT. |
| V2 | 22 August 2025 | Updated Version Published at ITT, with additional test requirements included. Updates have been marked with a V2 indicator. |
| V3 | 05 March 2026 | Updated version published at ITT to align with the clarifications provided in V6 of the Stability Feasibility Study Requirements document |

Contents

Version Control	2

Overview	3

1.	Solutions Details	3

2.	Steady State reactive power capability	4

3.	Feasibility Study Assumptions	5

3.1 Solution Reference e.g. [Company Name]-Bid1	5

4.	Feasibility study tests results and discussion e.g. [Company Name]-Bid1	6

4.1 Insert Solution Reference here e.g. [Company Name]-Bid1	6

4.1.1 Test 1 (Refer to Test 1 of the Technical Feasibility Study Guidance)	6

4.1.2 Test 2 (Refer to Test 2 of the Technical Feasibility Study Guidance)	9

4.1.3 Test 3 (Refer to Test 3 of the Technical Feasibility Study Guidance)	11

5.	List of Appendices / Attachments	15

# Overview

Solutions Details

The same solution reference/name should be used throughout the report and should be consistent with other tender documents and follow the format provided in the Technical Submission document e.g. [Company Name]–Bid1, [Company Name]–Bid2 etc

| Parent Company name |  |
| --- | --- |
| Solution location(s) | Please state all the Grid Entry Point (GEP) names and voltage levels for each solution considered in this report |
| List of solutions considered in this report | Please state all the solutions considered in this report (clearly stating which solutions relate to which substation locations). It is required that all solutions be submitted in one report. |
| Response: |  |
| Overview of solution | Please include a brief description of the solutions covered in this report. Approx. 100 words per solution |
| Response: |  |

Please complete Table 1 to show which solutions and technologies are considered at which locations. The same solution reference/name should be used throughout the report and should be consistent with other tender documents and follow the format provided the Technical Submission document (e.g. [Company Name] – Bid1, [Company Name] – Bid2 etc.)

Table 1: Solutions

| - Solution Reference | - Subsidiary SPV (if any) | - GEP name and voltage | - Technology Type * | - Rated Power (MVA) | - Max MW Export | - Max MW import |
| --- | --- | --- | --- | --- | --- | --- |

- *GBGF-S, GBGF-I or Hybrid

Steady State reactive power capability

Please copy and complete Table 2 for each solution. Describe any capping of the reactive power output under any condition not mentioned in Table 2. Please note that all values must specified to 3 decimal places.

Table 2: Solution 1 Reactive Power Range at GEP

Solution: Insert Solution Reference here e.g. [Company Name]-Bid1.

| Purpose | GEP voltage (p.u) | Active Power Condition | MW at GEP | Lead MVAr at GEP | Lag MVAr at GEP | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Required service for (For GBGF-I and GBGF-S) | 0.95 | Maximum MW export |  |  |  |  |
|  |  | 0 MW |  |  |  |  |
|  |  | Maximum MW import |  |  |  |  |
|  | 1 | Maximum MW export |  |  |  |  |
|  |  | 0 MW |  |  |  |  |
|  |  | Maximum MW import |  |  |  |  |
|  | 1.05 | Maximum MW export |  |  |  |  |
|  |  | 0 MW |  |  |  |  |
|  |  | Maximum MW import |  |  |  |  |
| Required service for GBGF-I only For GBGF-S this is only for information. | 0.9 | Maximum MW export |  |  |  |  |
|  |  | 0 MW |  |  |  |  |
|  |  | Maximum MW import |  |  |  |  |
|  | 1.1 | Maximum MW export |  |  |  |  |
|  |  | 0 MW |  |  |  |  |
|  |  | Maximum MW import |  |  |  |  |

Feasibility Study Assumptions

Please use the format below to provide the assumptions made when undertaking the feasibility study. Please add a sub section for each solution.

## 3.1 Solution Reference e.g. [Company Name]-Bid1

| Response Format | For each proposed solution(s) provide: - A diagram of the simulation network used for the feasibility study clearly marking GEP and Solution. - V2 An explanation of the location of the Solution Terminals. For each simulation, the following must be met or explained: - The pre-fault voltage at the GEP should be 1 p.u. - The time step resolution should not be greater than 1ms and must clearly show current values pre-fault, during the fault and post fault period for up to a time when a post fault steady state is reached. - Simulation type (RMS or EMT) and the method of acquiring phasor quantities from the EMT simulation. - V3 A full explanation of how all quantities are obtained from the model - How events in all tests are modelled. - Network SCL and X/R values (Or network impedance values) used for each solution. - Asset and Solution parameters relevant to modelling - Confirmation that all controllers, tap changer positions and machine parameters do not change throughout the simulation. |
| --- | --- |
| Attachments | Please include the titles of any attachments associated to this section. |
| Response |  |

Feasibility study tests results and discussion e.g. [Company Name]-Bid1

Please use the format below to provide the feasibility study test results and associated commentary.

All tests are required for each solution. Please copy the template below for each solution e.g Section 4.1 would be for Bid 1 and Section 4.2 for Bid 2 etc.

## 4.1 Insert Solution Reference here e.g. [Company Name]-Bid1

## 4.1.1 Test 1 (Refer to Test 1 of the Technical Feasibility Study Requirements)

| Response Format | Text (No more than 500 words) and plots. The tenderer must: - V3 Insert Time series plots from Test 1 showing: - GEP Positive Sequence; Active, Reactive and Total Fault Current components. - GEP Voltage Magnitude - GEP Active and Reactive Power - V3 These time-series plots should show the overall performance of the plant in addition to the performance during the event. To achieve this providers may have to include two time-series plots, one zoomed in on the event and one showing the event as a whole. - State if there is any capping of the short circuit current output due to plant rating - Using all plots from test 1: - Show that the device injects fault current for a retained voltage without the need for measurement as described in Test 1. - Show the reactive fault current response time of 5ms and injection levels proportional to the size of the voltage event. - For GBGF-I, show that the reactive fault current has reached Peak Rating Current within 30ms of fault occurrence for Step 1-7. - For step 8 confirm that the fault impedance provided by NESO has been used to simulate the remote faults. |
| --- | --- |
| Attachments | Please include the titles of any attachments associated to this section. |
| Response |  |

Based on Test 1, please complete Table 3 (below). Please note that Step 8 will need to be completed for all specified reference points for the targeted locations. Each reference point will need to consider the relevant fault impedance for that location. Please note that some locations may have to simulate faults with respect to multiple Reference points within a region (e.g For Substation in North East England, South Wales and West England regions, South West England and North Scotland)

When filling the reactive component of fault current in Table 3, positive values must be used for capacitive current (reactive power injection) while negative values must be used for inductive currents (reactive power absorption). The value of effective SCL (the last column in Table 3 can be calculated by multiplying the reactive component of the fault current at GEP at 40ms by the corresponding effectiveness factors of the reference sites for the targeted locations in the “LT2029 Stability Effectiveness sheet” shared by NESO. Please note that all values must be specified to 3 decimal places

Table 3: Solution 1 Fault Current Contributions Based on Test 1

| Step | Pre Fault Conditions |  |  | Fault Condition |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Voltage Magnitude at GEP (p.u) | Active Power at GEP (MW) | Reactive Power at GEP (MVAr) | Fault Impedance |  | Voltage at GEP, 40ms after the fault (p.u.) | Total Fault Current Contribution of the solution at GEP at 40ms after the fault (kA) | Reactive Component of the fault at GEP at 40ms after the fault (kA) | Effective SCL at Ref point (MVA) [Step 8 Only] |
|  |  |  |  | R(Ω) | X(Ω) |  |  |  |  |
| 1 |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |
| 8a* |  |  |  |  |  |  |  |  |  |
| 8b* |  |  |  |  |  |  |  |  |  |
| 8c* |  |  |  |  |  |  |  |  |  |
| 8d* |  |  |  |  |  |  |  |  |  |

*If Required

## 4.1.2 Test 2 (Refer to Test 2 of the Technical Feasibility Study Requirements)

This test and section are required for all solutions for each technology type, rating and substation location.

| Response Format | Text (No more than 500 words) and plots. The tenderer must: - V3 Insert Time series plots from Test 2 showing: - GEP Positive Sequence, Active, Reactive and Total Fault Current components - GEP Active and Reactive Power - GEP Voltage Magnitude - GEP Frequency and RoCoF - Solution Terminals Positive Sequence, Active, Reactive and Total Fault Current components - Solution Terminals Active and Reactive Power - Solution Terminals Voltage Magnitude. - V3 These time-series plots should show the overall performance of the plant in addition to the performance during the event. To achieve this providers may have to include two time-series plots, one zoomed in on the event and one showing the event as a whole. - Show calculations of how inertia values relate to the plots of MW output and system frequency. - State inertia value in MJ or MW.s as explained in the technical specification in Table 3 below. - State if there is any capping of the inertia output due to device’s rating. It must be demonstrated that any capping does not occur for a RoCoF of 1Hz/s. - Show the inertial response is initiated within 5ms for step 9. - Describe how inertia is provided from the device, ensure that there is no requirement for measurement from the network or a Phase Locked Loop (PLL) to trigger the inertial response. - Identify any run modes or active power requirements (e..g generation output, state of the charge, terminal voltage, etc.) that limit the provision of inertia. - Show the solution’s response to step 10 and step 11. - V2 Show the solution’s response to Steps 12, 13, 14 and 15. - V2 Provide an explanation of the plant’s performance to the RoCoF events. |
| --- | --- |
| Attachments | Please include the titles of any attachments associated to this section. |
| Response |  |

Based on Test 2, please complete Table 4 below. Please not that all values must specified to 3 decimal places.

For both GBGF-S, GBGF-I and hybrid solutions the inertia values in MW.s should be computed through Equation 1. For each event the Active Inertia Power (∆P in Equation 1) should be based on an average across all recorded samples over the duration of the ramp event.

Equation 1: Inertia= ∆P f02 × RoCoF

Where:

∆P is the Active Inertia Power of the Grid Forming Plant for a frequency event of   1Hz/s (MW)

RoCoF is the Rate of Change of Frequency in Hz/s

f0 is the pre-fault System Frequency (Hz)

For the avoidance of doubt ∆P should be calculated as follows:

∆P = [Average MW provided by the solution at GEP across all the recorded samples over the frequency ramp period (1 second)] – [Initial MW provided by the solution prior to the event].

Table 4: Solution 1 Inertia Values based on Test 2

| Step | Pre Event Conditions |  |  | Event Conditions |  |
| --- | --- | --- | --- | --- | --- |
|  | Voltage Magnitude at GEP (p.u.) | Active Power at GEP (MW) | Reactive power at GEP (MVAr) | ΔP(MW) | Inertia (MW.s) |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| Minimum Inertia (MW.s) |  |  |  |  |  |

## 4.1.3 Test 3 (Refer to Test 3 of the Technical Feasibility Study Requirements)

This test and section are required for all solutions for each technology type, rating and substation location.

| Response Format | Text (No more than 500 words) and plots. The tenderer must: - V3 Insert Time series plots from Test 2 showing: - GEP Positive Sequence, Active, Reactive and Total Fault Current components - GEP Active and Reactive Power - GEP Voltage Magnitude - GEP Frequency - GEP Phase Angle - Solution Terminals Positive Sequence, Active, Reactive and Total Fault Current components - Solution Terminals Active and Reactive Power - Solution Terminals Voltage Magnitude. - Solutions Terminals Phase Angle - Indication if the plant is in the Withstand Mode. - V3 These time-series plots should show the overall performance of the plant in addition to the performance during the event. To achieve this providers may have to include two time-series plots, one zoomed in on the event and one showing the event as a whole. - Show that there is a response in active and/or reactive power within 5ms following a phase angle change - Explain if the solution is blocked or tripped under any test. - Explain any limitations in withstanding and providing support for the angle changes in Test 3 of the feasibility study guidance. - V3 For GBGF-I plant if an alternative Phase Angle Jump has been used this should be clearly explained. - V2 Provide an explanation of the plant’s performance. For GBGF-I solutions this must include an explanation of the voltage source behaviour, the implementation of any current limiting functions, and details of the Phase Angle Jump Limit of the plant. For each simulation it is required that an explanation of the performance is provided. V3 For GBGF-I plant this explanation should detail how any current limiting function is acting, if necessary, a plot showing the operation of the limiter should be included. It is expected that the following explanation of the limiter is provided at a minimum: - Influence on Sequence Components i.e. impact of Current Limiting algorithm used (virtual impedance for example) on the Positive, Negative and Zero Sequence components - Influence on Active and Reactive current components - If current limitation is achieved through the use of virtual impedance is it bound by time, current or both? How is this activated and deactivated? What is the threshold of the limitation and is this based upon instantaneous or RMS values of current. - Following the phase angle jump event how does the plant return to its previous operation point stably? |
| --- | --- |
| Attachments | Please include the titles of any attachments associated to this section. |
| Response |  |

Based on Test 3, please complete Table 5. Please note that all values must be specified to 3 decimal places.

V2 Table 5: Solution 1 Test 3 Summary

| Step | Pre Event Conditions |  |  | Event Condition |  |
| --- | --- | --- | --- | --- | --- |
|  | Voltage Magnitude at GEP (p.u.) | Active Power at GEP (MW) | Reactive Power at GEP (MVAr) | Simulated GEP Phase Angle Change (degrees) | Did the solution block or trip? [Yes/No] |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |
| 16 |  |  |  |  |  |
| 17 |  |  |  |  |  |
| 18 |  |  |  |  |  |
| 19 |  |  |  |  |  |
| 20 |  |  |  |  |  |
| 21 |  |  |  |  |  |
| 22 |  |  |  |  |  |
| 23 |  |  |  |  |  |
| 24 |  |  |  |  |  |

List of Appendices / Attachments

Study results and datasets for all tests in the feasibility guidance should be submitted along with this report and listed below.

| Appendix Number | Document | File name as submitted. |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |

V2 The latest version of the Feasibility Study should be considered.

Clearly Highlighting the fault current at 40ms following the fault.

V2 The latest version of the effectiveness data sheet should be considered.

V2 The latest version of the Feasibility Study should be considered.

V2 The latest version of the Feasibility Study should be considered.