Site Audit proposal

This is a great initiative. Since you have the TenneT "Uitwerking EMC eisen-zone concept" (Document E04), which contains specific detail drawings (e.g., "Detail 27", "Detail 13") and photos of "Good vs. Bad" installation practices, we should use that as the benchmark.

The goal of this table is to create a "Gap Analysis" view: Here is what TenneT requires (The Standard) vs. Here is what we found (The Reality).

Here are two recommended formats. Option 1 is best for the final report (Visual Comparison). Option 2 is best for the field engineer doing the inspection (Checklist).

# Option 1: The "Side-by-Side" Verification Table (Recommended for Final Report)

This format is powerful because it visually proves compliance or non-compliance to the client immediately.

| ID | Location / Zone | TenneT Requirement / Reference Detail | Site Observation (Photo) | Assessment & Action |
| --- | --- | --- | --- | --- |
| OBS-01 | Location: CDG - Telecom RoomZone: LPZ 2 | Requirement: AM-Req-6096.01 / Detail 2.2Standard: Cable entry must use EMC-frame (Roxtec) connected to earthing busbar.(Insert snippet of "Detail 27" or TenneT reference photo here) | (Insert Photo taken on site)Photo ID: IMG_2025_001.jpg | Status: <span style="color:red">Non-Compliant</span>Finding: Cable entry frame is present but earthing strap to ring earth is disconnected.Action for DP2-4: Re-establish earthing connection during DP2-4 cabling works. |
| OBS-02 | Location: Field - Takhuisje 1Zone: LPZ 1 | Requirement: AM-Req-1326.02Standard: Concrete cable trench must contain Parallel Earthing Conductor (PEC) ≥ 50mm² Cu.(Insert snippet of TenneT PEC requirement) | (Insert Photo taken on site)Photo ID: IMG_2025_004.jpg | Status: <span style="color:green">Compliant</span>Finding: 50mm² Cu PEC visible in trench, connected to earthing grid.Action for DP2-4: Connect new DP2-4 trench PECs to this existing point. |

# Option 2: The Field Inspection Log (Excel Format)

Use this format for the actual site walk-down. It allows you to filter by "Asset" or "Status" later.

| ID | Asset / System | Location | TenneT Ref (E04/VS1) | Requirement Summary | Photo Ref | Observation / Deviation | Status (OK/NOK) | Impact on DP2-4 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Cable Entry | CDG - AC Room | Detail 27 / AM-Req-0905 | Cables must be earthed at entry frame. | IMG_01 | Earthing present but corroded. | NOK | Needs cleaning/replacement. |
| 2 | Cabinet | Takhuisje 3 | AM-Req-6096 | EMC Glands (Wartels) must be used. | IMG_02 | Plastic glands used on shielded cable. | NOK | Replace with EMC glands. |
| 3 | Earthing | Field - Bay 1 | AM-Req-1248 | Structure earthing 2x connections. | IMG_03 | Visual check confirms 2 connections. | OK | None. |

# How to use the "TenneT E04" Document in this process:

The document "Uitwerking EMC eisen-zone concept standaard 380kV station" is your "Answer Key." pre-populate the table before going to site with the key checks based on that document.

Pre-fill your inspection sheet with these specific checks (derived from the PDF):

- Civil/Building (Bouwkundig):

  - Check: Is the rebar in the concrete connected to the earthing system at max 5m intervals? (Ref: Bijlage 2.1)

  - Check: Are metal door frames connected to the wall mesh/earth? (Ref: Bijlage 2.5)

- Cable Entry (Kabelinvoer):

  - Check: Are Roxtec frames used? Are they earthed to the ring earth? (Ref: Detail 27 / Bijlage 2.2)

  - Check: Are cable shields stripped and clamped inside the EMC module (or right after)?

- Cabinets (Kasten):

  - Check: Do cabinets have EMC wartel-plates (gland plates) at the bottom? (Ref: Bijlage 1, Section I.B)

  - Check: Are "pigtails" (long earth wires) used? (Bad practice - check against Foto 9963 in the PDF).

  - Check: Are EMC "brievenbus" (letterbox) entries used where glands don't fit? (Ref: Foto 1158).

- Cable Routing (Kabeltracés):

  - Check: Is there a PEC (Parallel Earthing Conductor) in the concrete trench? (Ref: Bijlage 4).

  - Check: Are cables segregated (HV vs LV vs Data)?

Combining these show that:

- You have already studied the specific TenneT E04 standard.

- You aren't just taking random photos; you are performing a compliance audit against specific TenneT "AM-Req" codes.

- You are focused on the solution for DP2-4, not just listing problems in DP1.